## Pipe Calcs
Simple Pipe & Fitting Calculations
Joe Evans, Ph.D 12/26/12
Pipe Calcs |  | Pipe Type | C Range | C Average | Commonly Used
Enter the required data in the yellow cells |  | Cast / Ductile Iron - New | 150 - 80 | 130 | 100
|  | Cast Iron 10 years old | 113 - 107
Pipe Segment 1 |  | Cast Iron 20 years old | 100 - 89
Flow Rate (GPM) | 550 | Cast Iron 30 years old | 75 - 90
Pipe ID (Inches) | 4 | Cast Iron 40 years old | 83 - 64
Pipe Length (Feet) | 30 | Tar Coated Cast Iron | 145 - 50 | 130 | 100
Hazen & Williams C Value | 130 | Steel - New | 150 - 80 | 130 | 100
|  | Corrugated Steel |  | 60 | 60
Calculated Results |  | Cement Lined Iron / Steel | 160 - 130 | 148 | 140
Velocity in Ft/sec | 14.0422 | Asphalt Lined Iron / Steel | 140 - 130
Velocity Head in Ft | 3.0618 | Copper, Brass, Lead, Glass | 150 - 120 | 140 | 130
Friction / 100 Feet of Pipe | 17.9265 | Aluminum | 150 - 130
Total Pipe Friction | 5.3779 | Concrete | 152 - 85 | 120 | 100
Fitting Equivalent Length | 46.38 | Asbestos Cement | 140
Total Fitting Friction | 8.3143 | PVC | 160 - 150 | 155 | 150
Total Friction Losses Segment 1 | 13.6922 | PE | 140
Pipe Segment 2 |  | Instructions
Flow Rate (GPM) | 550 | This spreadsheet is designed to calculate pipe and fitting friction for one
Pipe ID (Inches) | 6 | to three pipe segments. The Hazen & Williams equation and C values are
Pipe Length (Feet) | 1000 | used for all friction calculations. This provides flexibility when working
Hazen & Williams C Value | 100 | with both new and old piping systems.
Calculated Results |  | Enter the required data in the four yellow cells for one, two or three pipe
Velocity in Ft/sec | 6.241 | segments. The calculated results will appear below. Click on the Fitting
Velocity Head in Ft | 0.60481 | Calcs tab to enter the fitting data. Click on the box that corresponds to a
Friction / 100 Feet of Pipe | 4.0527 | desired fitting and its size. Enter the number of fittings used in that pipe
Total Pipe Friction | 40.5271 | pipe section. Enter the quantities of any other fittings in the appropriate box.
Fitting Equivalent Length | 24.28 | Note that each pipe section has its own fitting selector. If a particular fitting
Total Fitting Friction | 0.984 | is not shown, you may enter it manually in one of the bottom lines. You will
Total Friction Losses Segment 2 | 41.5111 | have to look up the "equivalent pipe length" and enter it in Column Q. The
Total Friction Losses 1 & 2 | 55.2034 | value should be the total equivalent length for the number of fittings you
entered. Fitting equivalent length and total fitting friction will be displayed
Pipe Segment 3 |  | in the calculated results for each pipe section.
Flow Rate (GPM)
Pipe ID (Inches) |  | The example included is for a submersible sewage pump. Pipe segment 1 runs
Pipe Length (Feet) |  | from the pump connection inside the wet well to a valve box located outside
Hazen & Williams C Value |  | the wet well. It includes 30' of 4" pipe, a 90 deg elbow, a check valve and a
gate valve. Segment 2 runs from the valve box to a gravity main. It includes
Calculated Results |  | 1000' of 6" pipe, two 45 deg elbows and two gate valves. The total friction for
Velocity in Ft/sec | #DIV/0! | Segment 1 is 13.7' and the total for Segment 2 is 41.5'. The combined losses for
Velocity Head in Ft | #DIV/0! | both segments is 55.2'.
Friction / 100 Feet of Pipe | #DIV/0!
Total Pipe Friction | #DIV/0!
Fitting Equivalent Length | 0
Total Fitting Friction | #DIV/0!
Total Friction Losses Segment 3 | #DIV/0!
Total Friction Losses 1, 2 & 3 | #DIV/0!

## Fitting Calcs
Simple Pipe & Fitting Calculations
Joe Evans, Ph.D 12/16/12
Fitting Calcs
Enter the number of fittings in the yellow cells that correspond to the pipe diameter. All others must remain blank.
Pipe Segment 1
Fittings | 2" | 2.5" | 3" | 4" | 5" | 6" | 8" | 10" | 12" | 14" | 16" | 18" | 20" | 24"
90 Standard Elbow |  |  |  | 1 | [10 empty] | 10.1
90 Long Radius Elbow | [14 empty] | 0
45 Standard Elbow | [14 empty] | 0
Standard Tee (Branch Flow) | [14 empty] | 0
Standard Tee (Thru Flow) | [14 empty] | 0
Gate Valve |  |  |  | 1 | [10 empty] | 2.68
Globe Valve | [14 empty] | 0
Butterfly Valve | [14 empty] | 0
180 Return Bend | [14 empty] | 0
Swing Check Valve |  |  |  | 1 | [10 empty] | 33.6
[15 empty] | 46.38 | Total Losses In Equivalent Feet of Pipe
Calcs std 90 | 0 | 0 | 0 | 10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
long 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
branch tee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
thru tee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
gate | 0 | 0 | 0 | 2.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
globe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
bfly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
bend | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
swing check | 0 | 0 | 0 | 33.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
disc check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pipe Segment 2
Fittings | 2" | 2.5" | 3" | 4" | 5" | 6" | 8" | 10" | 12" | 14" | 16" | 18" | 20" | 24"
90 Standard Elbow | [14 empty] | 0
90 Long Radius Elbow | [14 empty] | 0
45 Standard Elbow | [5 empty] | 2 | [8 empty] | 16.2
Standard Tee (Branch Flow) | [14 empty] | 0
Standard Tee (Thru Flow) | [14 empty] | 0
Gate Valve | [5 empty] | 2 | [8 empty] | 8.08
Globe Valve | [14 empty] | 0
Butterfly Valve | [14 empty] | 0
180 Return Bend | [14 empty] | 0
Swing Check Valve | [14 empty] | 0
[15 empty] | 24.28 | Total Losses In Equivalent Feet of Pipe
Calcs std 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
long 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 0 | 0 | 0 | 0 | 0 | 16.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
branch tee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
thru tee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
gate | 0 | 0 | 0 | 0 | 0 | 8.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
globe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
bfly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
bend | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
swing check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
disc check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pipe Segment 3
Fittings | 2" | 2.5" | 3" | 4" | 5" | 6" | 8" | 10" | 12" | 14" | 16" | 18" | 20" | 24"
90 Standard Elbow | [14 empty] | 0
90 Long Radius Elbow | [14 empty] | 0
45 Standard Elbow | [14 empty] | 0
Standard Tee (Branch Flow) | [14 empty] | 0
Standard Tee (Thru Flow) | [14 empty] | 0
Gate Valve | [14 empty] | 0
Globe Valve | [14 empty] | 0
Butterfly Valve | [14 empty] | 0
180 Return Bend | [14 empty] | 0
Swing Check Valve | [14 empty] | 0
[15 empty] | 0 | Total Losses In Equivalent Feet of Pipe
Calcs std 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
long 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
branch tee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
thru tee | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
gate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
globe | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
bfly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
bend | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
swing check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
disc check | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0