## HPSA
Wastewater Pump Selection Assistant with "Auto Plot"
[6 empty] | Joe Evans, Ph.D 3/26/05 | [6 empty] | http://www.pumped101.com
Follow the five steps below to compare the operation of the same pump in a "pump down" application
versus VFD control in a "level control" environment. Scroll down for more detailed instructions.
AFFINITY LAW CALCULATOR
[6 empty] | 1) Enter the pump description in the yellow box to the right | [7 empty] | Submersible Non Clog S12L - 1150 RPM - 14.25" Trim
| ENTER RPM IN CELL B22 |  |  |  |  | 2) Enter eight 60 hertz flows In Q1 - Q8 (Cells H19 - O219)
Enter the corresponding heads (in ft) in H1 - H8 (Cells P19 - W219)
HERTZ | RPM | D Q | D H | D HP
[6 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
60 | 3600 | 100% | 100% | 100% |  | 0 | 1000 | 2000 | 3000 | 4000 | 5000 | 6000 | 7000 | 90 | 77 | 68 | 63 | 57 | 48 | 37 | 24
59 | 3540 | 98.33% | 96.69% | 95.08% | 59 | 0 | 983.3333 | 1966.6667 | 2950 | 3933.3333 | 4916.6667 | 5900 | 6883.3333 | 87.025 | 74.4547 | 65.7522 | 60.9175 | 55.1158 | 46.4133 | 35.7769 | 23.2067 |  | HP Calculations
58 | 3480 | 96.67% | 93.44% | 90.33% | 58 | 0 | 966.6667 | 1933.3333 | 2900 | 3866.6667 | 4833.3333 | 5800 | 6766.6667 | 84.1 | 71.9522 | 63.5422 | 58.87 | 53.2633 | 44.8533 | 34.5744 | 22.4267 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8
57 | 3420 | 95% | 90.25% | 85.74% | 57 | 0 | 950 | 1900 | 2850 | 3800 | 4750 | 5700 | 6650 | 81.225 | 69.4925 | 61.37 | 56.8575 | 51.4425 | 43.32 | 33.3925 | 21.66 | #DIV/0! | 60.7639 | 64.7989 | 70.1872 | 75.7576 | 77.7001 | 76.7954 | 73.1452
56 | 3360 | 93.33% | 87.11% | 81.3% | 56 | 0 | 933.3333 | 1866.6667 | 2800 | 3733.3333 | 4666.6667 | 5600 | 6533.3333 | 78.4 | 67.0756 | 59.2356 | 54.88 | 49.6533 | 41.8133 | 32.2311 | 20.9067
55 | 3300 | 91.67% | 84.03% | 77.03% | 55 | 0 | 916.6667 | 1833.3333 | 2750 | 3666.6667 | 4583.3333 | 5500 | 6416.6667 | 75.625 | 64.7014 | 57.1389 | 52.9375 | 47.8958 | 40.3333 | 31.0903 | 20.1667 | #DIV/0! | 46.8037 | 49.9117 | 54.062 | 58.3526 | 59.8488 | 59.152 | 56.3405
54 | 3240 | 90% | 81% | 72.9% | 54 | 0 | 900 | 1800 | 2700 | 3600 | 4500 | 5400 | 6300 | 72.9 | 62.37 | 55.08 | 51.03 | 46.17 | 38.88 | 29.97 | 19.44
53 | 3180 | 88.33% | 78.03% | 68.92% | 53 | 0 | 883.3333 | 1766.6667 | 2650 | 3533.3333 | 4416.6667 | 5300 | 6183.3333 | 70.225 | 60.0814 | 53.0589 | 49.1575 | 44.4758 | 37.4533 | 28.8703 | 18.7267
52 | 3120 | 86.67% | 75.11% | 65.1% | 52 | 0 | 866.6667 | 1733.3333 | 2600 | 3466.6667 | 4333.3333 | 5200 | 6066.6667 | 67.6 | 57.8356 | 51.0756 | 47.32 | 42.8133 | 36.0533 | 27.7911 | 18.0267
51 | 3060 | 85% | 72.25% | 61.41% | 51 | 0 | 850 | 1700 | 2550 | 3400 | 4250 | 5100 | 5950 | 65.025 | 55.6325 | 49.13 | 45.5175 | 41.1825 | 34.68 | 26.7325 | 17.34
50 | 3000 | 83.33% | 69.44% | 57.87% | 50 | 0 | 833.3333 | 1666.6667 | 2500 | 3333.3333 | 4166.6667 | 5000 | 5833.3333 | 62.5 | 53.4722 | 47.2222 | 43.75 | 39.5833 | 33.3333 | 25.6944 | 16.6667 | #DIV/0! | 35.1643 | 37.4994 | 40.6176 | 43.8412 | 44.9653 | 44.4418 | 42.3294
49 | 2940 | 81.67% | 66.69% | 54.47% | 49 | 0 | 816.6667 | 1633.3333 | 2450 | 3266.6667 | 4083.3333 | 4900 | 5716.6667 | 60.025 | 51.3547 | 45.3522 | 42.0175 | 38.0158 | 32.0133 | 24.6769 | 16.0067
48 | 2880 | 80% | 64% | 51.2% | 48 | 0 | 800 | 1600 | 2400 | 3200 | 4000 | 4800 | 5600 | 57.6 | 49.28 | 43.52 | 40.32 | 36.48 | 30.72 | 23.68 | 15.36
47 | 2820 | 78.33% | 61.36% | 48.07% | 47 | 0 | 783.3333 | 1566.6667 | 2350 | 3133.3333 | 3916.6667 | 4700 | 5483.3333 | 55.225 | 47.2481 | 41.7256 | 38.6575 | 34.9758 | 29.4533 | 22.7036 | 14.7267
46 | 2760 | 76.67% | 58.78% | 45.06% | 46 | 0 | 766.6667 | 1533.3333 | 2300 | 3066.6667 | 3833.3333 | 4600 | 5366.6667 | 52.9 | 45.2589 | 39.9689 | 37.03 | 33.5033 | 28.2133 | 21.7478 | 14.1067
45 | 2700 | 75% | 56.25% | 42.19% | 45 | 0 | 750 | 1500 | 2250 | 3000 | 3750 | 4500 | 5250 | 50.625 | 43.3125 | 38.25 | 35.4375 | 32.0625 | 27 | 20.8125 | 13.5 | #DIV/0! | 25.6348 | 27.337 | 29.6102 | 31.9602 | 32.7797 | 32.398 | 30.8582
44 | 2640 | 73.33% | 53.78% | 39.44% | 44 | 0 | 733.3333 | 1466.6667 | 2200 | 2933.3333 | 3666.6667 | 4400 | 5133.3333 | 48.4 | 41.4089 | 36.5689 | 33.88 | 30.6533 | 25.8133 | 19.8978 | 12.9067
43 | 2580 | 71.67% | 51.36% | 36.81% | 43 | 0 | 716.6667 | 1433.3333 | 2150 | 2866.6667 | 3583.3333 | 4300 | 5016.6667 | 46.225 | 39.5481 | 34.9256 | 32.3575 | 29.2758 | 24.6533 | 19.0036 | 12.3267
42 | 2520 | 70% | 49% | 34.3% | 42 | 0 | 700 | 1400 | 2100 | 2800 | 3500 | 4200 | 4900 | 44.1 | 37.73 | 33.32 | 30.87 | 27.93 | 23.52 | 18.13 | 11.76
41 | 2460 | 68.33% | 46.69% | 31.91% | 41 | 0 | 683.3333 | 1366.6667 | 2050 | 2733.3333 | 3416.6667 | 4100 | 4783.3333 | 42.025 | 35.9547 | 31.7522 | 29.4175 | 26.6158 | 22.4133 | 17.2769 | 11.2067
40 | 2400 | 66.67% | 44.44% | 29.63% | 40 | 0 | 666.6667 | 1333.3333 | 2000 | 2666.6667 | 3333.3333 | 4000 | 4666.6667 | 40 | 34.2222 | 30.2222 | 28 | 25.3333 | 21.3333 | 16.4444 | 10.6667 | #DIV/0! | 18.0041 | 19.1997 | 20.7962 | 22.4467 | 23.0222 | 22.7542 | 21.6727
39 | 2340 | 65% | 42.25% | 27.46% | 39 | 0 | 650 | 1300 | 1950 | 2600 | 3250 | 3900 | 4550 | 38.025 | 32.5325 | 28.73 | 26.6175 | 24.0825 | 20.28 | 15.6325 | 10.14
38 | 2280 | 63.33% | 40.11% | 25.4% | 38 | 0 | 633.3333 | 1266.6667 | 1900 | 2533.3333 | 3166.6667 | 3800 | 4433.3333 | 36.1 | 30.8856 | 27.2756 | 25.27 | 22.8633 | 19.2533 | 14.8411 | 9.6267
37 | 2220 | 61.67% | 38.03% | 23.45% | 37 | 0 | 616.6667 | 1233.3333 | 1850 | 2466.6667 | 3083.3333 | 3700 | 4316.6667 | 34.225 | 29.2814 | 25.8589 | 23.9575 | 21.6758 | 18.2533 | 14.0703 | 9.1267
36 | 2160 | 60% | 36% | 21.6% | 36 | 0 | 600 | 1200 | 1800 | 2400 | 3000 | 3600 | 4200 | 32.4 | 27.72 | 24.48 | 22.68 | 20.52 | 17.28 | 13.32 | 8.64
35 | 2100 | 58.33% | 34.03% | 19.85% | 35 | 0 | 583.3333 | 1166.6667 | 1750 | 2333.3333 | 2916.6667 | 3500 | 4083.3333 | 30.625 | 26.2014 | 23.1389 | 21.4375 | 19.3958 | 16.3333 | 12.5903 | 8.1667 | #DIV/0! | 12.0614 | 12.8623 | 13.9318 | 15.0375 | 15.4231 | 15.2435 | 14.519
34 | 2040 | 56.67% | 32.11% | 18.2% | 34 | 0 | 566.6667 | 1133.3333 | 1700 | 2266.6667 | 2833.3333 | 3400 | 3966.6667 | 28.9 | 24.7256 | 21.8356 | 20.23 | 18.3033 | 15.4133 | 11.8811 | 7.7067
33 | 1980 | 55% | 30.25% | 16.64% | 33 | 0 | 550 | 1100 | 1650 | 2200 | 2750 | 3300 | 3850 | 27.225 | 23.2925 | 20.57 | 19.0575 | 17.2425 | 14.52 | 11.1925 | 7.26
32 | 1920 | 53.33% | 28.44% | 15.17% | 32 | 0 | 533.3333 | 1066.6667 | 1600 | 2133.3333 | 2666.6667 | 3200 | 3733.3333 | 25.6 | 21.9022 | 19.3422 | 17.92 | 16.2133 | 13.6533 | 10.5244 | 6.8267
31 | 1860 | 51.67% | 26.69% | 13.79% | 31 | 0 | 516.6667 | 1033.3333 | 1550 | 2066.6667 | 2583.3333 | 3100 | 3616.6667 | 24.025 | 20.5547 | 18.1522 | 16.8175 | 15.2158 | 12.8133 | 9.8769 | 6.4067
30 | 1800 | 50% | 25% | 12.5% | 30 | 0 | 500 | 1000 | 1500 | 2000 | 2500 | 3000 | 3500 | 22.5 | 19.25 | 17 | 15.75 | 14.25 | 12 | 9.25 | 6 | #DIV/0! | 7.5955 | 8.0999 | 8.7734 | 9.4697 | 9.7125 | 9.5994 | 9.1432
[7 empty] | 100 | 77 | 58
[5 empty] | 60 | H1: 38.961; H2: 33.3333; H3: 29.4372; H4: 27.2727; H5: 24.6753; H6: 20.7792; H7: 16.0173; H8: 10.3896
[5 empty] | 55 | H1: 32.7381; H2: 28.0093; H3: 24.7354; H4: 22.9167; H5: 20.7341; H6: 17.4603; H7: 13.459; H8: 8.7302
[5 empty] | 50 | H1: 27.0563; H2: 23.1481; H3: 20.4425; H4: 18.9394; H5: 17.1356; H6: 14.43; H7: 11.1231; H8: 7.215
[5 empty] | 45 | H1: 21.9156; H2: 18.75; H3: 16.5584; H4: 15.3409; H5: 13.8799; H6: 11.6883; H7: 9.0097; H8: 5.8442
[5 empty] | 40 | H1: 17.316; H2: 14.8148; H3: 13.0832; H4: 12.1212; H5: 10.9668; H6: 9.2352; H7: 7.1188; H8: 4.6176
[5 empty] | 35 | H1: 13.2576; H2: 11.3426; H3: 10.0168; H4: 9.2803; H5: 8.3965; H6: 7.0707; H7: 5.4503; H8: 3.5354 |  | Low Level
[6 empty] | H1: 9.7403; H2: 8.3333; H3: 7.3593; H4: 6.8182; H5: 6.1688; H6: 5.1948; H7: 4.0043; H8: 2.5974 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
[6 empty] | 3) To plot a system (control level) curve, enter the system | [7 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
[6 empty] | heads (in ft) in SH1 - SH8 (Cells P61 - W61) that correspond | [7 empty] | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
| INSTRUCTIONS: | [12 empty] | 19.4805 | 19.4805 | 19.4805 | 19.4805 | 19.4805 | 19.4805 | 19.4805 | 19.4805
to the flows in Q1 - Q8. (See Instructions below)
4) Enter "pump down" level (in ft) in the yellow box
[6 empty] | to the right (Cell P66). (See instructions below) | [7 empty] | SH1: 10
[6 empty] | 5) Enter the pump's hydraulic efficiencies in Ef 1 - Ef 8 | [7 empty] | Ef 1 | Ef 2 | Ef 3 | Ef 4 | Ef 5 | Ef 6 | Ef 7 | Ef 8
[6 empty] | (Cells P70-W70) that correspond to the flows in Q1 - Q8 | [8 empty] | 0.32 | 0.53 | 0.68 | 0.76 | 0.78 | 0.73 | 0.58
Enter as a decimal equivalent. (See instructions below)
Click on the "Level Control" and "Pump Down" tabs to view pump performance.
| AFFINITY LAW CALCULATOR | [5 empty] | HPSA Instructions
The Hydromatic Pump Selection Assistant (HPSA) allows you to compare the operating frequency range of a given pump
to the system conditions it must match in a level control or Constant Pressure / Variable Flow (CP/VF) application. You
can evaluate different pumps so that you can select the one that offers the best power savings and range of control. It
also allows you to demonstrate the advantages of level control over pump down in many applications. For an over view of
pump down vs level control, download "VFD Pump Selection - - Level Control" from my web site.
Frequency and pump speed are synonymous, so the actual speed of the pump is not important. What is important is the
frequency (or speed) range. It is this range that dictates the potential power savings attainable by the application when
operating in a variable speed mode.
Step 1
Enter the pump description as you would like it to appear on the charts.
Step 2
| Enter a motor speed for 60 Hz | [5 empty] | Auto Plot requires that you enter eight, 60 Hz operating points in the row with the yellow background. Flows are entered
| operation in the cell with the | [5 empty] | beneath Q1 - Q8 and the corresponding heads are entered beneath H1 - H8. It is not necessary to begin with shutoff head
| yellow background and motor | [5 empty] | unless the pump will operate to the far left of the curve. Corresponding flows and heads are calculated for each point from
| speeds at the lower frequencies | [5 empty] | 59 - 30 Hz, however, Auto Plot displays the curves in 5hz increments (i.e. 55, 50, 45, etc). The labels displayed at each
| will be displayed. Note that the | [5 empty] | xy intercept on the head / capacity curves is the BHP required at that point.
Step 3
In a level control application, the system curve is the TDH required to reach some elevation above the controlled level of the
waste water in the wet well. In a pump down application, it is level at which the pump starts. Often they will be the same.
In the case of a "free flow" application, the curve will be flat. If the pump is pumping into a pipe line friction may enter the
picture at some point along the curve. In this case the curve will slope upwards as capacity increases.
Enter the calculated system head for each flow point (Q1 - Q8) in SH1 - SH8.
Step 4
The "pump down level" of a pump down application is defined is the vertical distance (in ft) between the elevation at which the
pump starts and the elevation at which it shuts off. Enter the distance in the yellow box.
Step 5
HPSA calculates BHP at each xy intercept on the head / capacity curves using the equation (q*h) / (3960*eff). Enter the
hydraulic efficiency of points Q1 - Q8 in Ef 1 - Ef 8. Enter as a decimal equivalent, not a whole number. If Q1 is zero,
leave Ef 1 blank.
Click on the Level Control and Pump Down Tabs to view the results.
The Example
| they are a function of frequency | [5 empty] | The example included with the HPSA shows a S12L (1150 RPM) with a maximum flow of 7000 gpm and a shut off head of 90'. The
| and not relative motor speed. | [5 empty] | system curve indicates that a constant pressure of 45 feet is required to maintain the predetermined level in "level control" mode.
The system curve also defines the upper (or pump on) level of the pump down application. The "pump down level" or low level
line shows that the pump must be able to reach a TDH of 65' to satisfy the pump down application.
| The example included with the | [5 empty] | If you click on the Pump Down tab, you will see that the S12L will meet the requirements of the pump down application over
| calculator shows a 60 Hz motor | [5 empty] | a flow range of 2000 to approximately 5300 gpm. At maximum flow the BHP required is approximately 78. At minimum flow
| speed of 3450 RPM. | [5 empty] | the BHP drops to 65. (For you math types, a differential equation could be employed to calculate the average BHP required to pump
the pit from the upper to the lower level (if we know the volume).)
If you click on the Level Control tab you will see that the S12L will meet these same requirements under VFD control but with a
significant advantage. At maximum flow the BHP requirement is the same - - 78. But, at 2000 gpm BHP is reduced to approximately
38 - - a savings of about 27 hp. At 4000 gpm the savings is about 18 hp and at 3000 gpm the savings is about 25 hp.
If you would like more information on VFD operation or sizing pumps for various VFD applications go to:
www.pumped101.com